## EMC
[14 empty] | Comparison of EMC requirements, | [5 empty] | Blue: Table B.1 – Non-residential (Industrial)
[14 empty] | climate and mechanical tests | [5 empty] | Green:Table B.2 Residential area
[14 empty] | between supply device and supply point measuring device | [5 empty] | Yellow: Table C.1 – Requirements from DIN EN 50470-1 (VDE 0418-0-1) /DIN EN 50470-3 (VDE 0418-0-3)
Spalte1 | Spalte2 | Spalte3 | Spalte4 | Spalte5 | Spalte6 | Spalte7 | Spalte8 | Spalte9 | Spalte10 | Spalte11 | Spalte12 | Spalte13 | Spalte14 | Spalte15 | Spalte1 | Spalte2 | Spalte3 | Spalte4 | Spalte5 | Spalte6 | Spalte7 | Spalte8 | Spalte9 | Spalte10 | Spalte11 | Spalte12 | Spalte1 | Spalte2 | Spalte3 | Spalte4 | Spalte5 | Spalte6 | Spalte7 | Spalte8 | Spalte9 | Spalte10 | Spalte11 | Spalte12 | Spalte13 | Spalte14 | Spalte15 | Spalte16
[5 empty] | Table B.1 – Non-residential (Industrial) | [11 empty] | Table B.2 Residential area | [10 empty] | Table C.1 – Requirements from DIN EN 50470-1 (VDE 0418-0-1) /DIN EN 50470-3 (VDE 0418-0-3)
|  |  |  | Phenomenon | Basic Standard | Demand | Operating Mode | Utility Facility | Counters and Additional Equipment | [5 empty] | Phenomenon | Basic Standard | Demand | Operating | Utility facility | Counters and Accessories | [6 empty] | Phenomenon | Basic Standard | Demand | LME
[8 empty] | Evaluation Criterion | Evaluation Criterion | [8 empty] | mode | Evaluation Criterion | Evaluation Criterion | [9 empty] | Evaluation Criterion
|  |  |  | ESD | DIN EN 61000-4-2 | Air discharge: 8kV | BA1, BA2 | B | – | [5 empty] | ESD | DIN EN 61000-4-2 | Air discharge: 8KV | BA1, BA2 | B | – | [6 empty] | ESD | DIN EN 61000-4-2 | Air discharge: 15 kV | B
[5 empty] | (VDE 0847-4-2) | Contact discharge: 4KV | [9 empty] | (VDE 0847-4-2) | Contact discharge: 4kV | [10 empty] | (VDE 0847-4-2) | contact discharge: 8 kV, | Critical change value / CRC memory areas
[6 empty] | Air discharge: 15 kV | BA2 | – | B | [7 empty] | Air discharge: 15KV | BA2 | – | B | [8 empty] | Number: 10
[6 empty] | Contact discharge: 8KV |  |  | Critical change value / CRC memory areas | [7 empty] | Contact discharge: 8kV |  |  | Critical change value/CRC memory areas | [6 empty] | Immunity to interference | DIN EN 61000-4-3 | 80MHz to 2000MHz | A
[6 empty] | Number: 10 | [8 empty] | Immunity to interference | DIN EN 61000-4-3 | 3V/m, 80MHz to 1000MHz | BA1, BA2 | A | – | [7 empty] | (VDE 0847-4-3) | 80% AM, 1kHz | Percentage deviation
|  |  |  | Immunity to interference | DIN EN 61000-4-3 | 10V/m, 80MHz to 1000MHz | BA1, BA2 | A | – | [6 empty] | (VDE 0847-4-3) | 80% AM, 1kHz | [11 empty] | 10V/m
[5 empty] | (VDE 0847-4-3) | 80% AM, 1kHz | [10 empty] | 3V/m, 1.4GHz to 2GHz | BA1, BA2 | A | – | [8 empty] | 80MHz to 2000MHz | B
[6 empty] | 3V/m, 1.4GHz to 2GHz | BA1, BA2 | A | – | [7 empty] | 80% AM, 1kHz | [11 empty] | 80% AM, 1kHz | Critical change value/CRC memory areas
[6 empty] | 80% AM, 1kHz | [10 empty] | 3V/m, 2GHz to 2.7GHz | BA1, BA2 | A | – | [8 empty] | 30V/m
[6 empty] | 3V/m, 2GHz to 2.7GHz | BA1, BA2 | A | – | [7 empty] | 80% AM, 1kHz | [9 empty] | BURST | DIN EN 61000-4-4 | Power input: 4kV/60s/5kHz, CM | –
[6 empty] | 80% AM, 1kHz | [10 empty] | 80MHz to 2000MHz | BA3 | – | A | [7 empty] | (VDE 0847-4-4) | Auxiliary circuits > 40 V: 2 kV/60 s/5 kHz | B
[6 empty] | 80MHz to 2000MHz | BA3 | – | A | [7 empty] | 80% AM, 1kHz |  |  | Critical change value/CRC memory areas | [8 empty] | Control lines 1 kV/60 s/5 kHz | Percentage deviation
[6 empty] | 80% AM, 1kHz |  |  | Percentage deviation | [7 empty] | 10V/m | [9 empty] | SURG | DIN EN 61000-4-5 | 1.2/50 μs, DM, phase angle 60°, 240° | B
[6 empty] | 10V/m | [10 empty] | 80MHz to 2000MHz | BA2 | – | B | [7 empty] | (VDE 0847-4-5) | Current/Voltage Circuit: 4kV, 2Ω | Critical change value/CRC memory areas
[6 empty] | 80MHz to 2000MHz | BA2 | – | B | [7 empty] | 80% AM, 1kHz |  |  | Temporary functional failure permitted without loss of data/CRC memory areas relevant to calibration law | [8 empty] | Auxiliary circuits > 40 V: 1 kV, 42 Ω
[6 empty] | 80% AM, 1kHz |  |  | Critical change value / CRC memory areas | [7 empty] | 30V/m | [11 empty] | Pulse number: 5 positive, 5 negative
[6 empty] | 30V/m | [9 empty] | DIN EN 61000-4-4 | Power consumption: 2kV/5kHz | BA1, BA2 | B | – | [8 empty] | Repetition rate: 1/min
|  |  |  | BURST | DIN EN 61000-4-4 | Power supply: 4kV/5kHz | BA1, BA2 | B | – | [5 empty] | BURST | (VDE 0847-4-4) | I/O line: 1kV / 5kHz | [9 empty] | Conducted immunity | DIN EN 61000-4-6 | 150kHz to 80MHz, | A
[5 empty] | (VDE 0847-4-4) | Data lines: 2kV/5kHz | [10 empty] | Power cord: 4kV/60s/5kHz, CM | BA3 | – | B | [7 empty] | (VDE 0847-4-6) | 80% AM, 1kHz | Percentage deviation
[6 empty] | Power input: 4kV/60s/5kHz, CM | BA3 | – | B | [7 empty] | Auxiliary circuits > 40 V: 2 kV/60 s/5 kHz |  |  | Critical change value/CRC memory areas | [8 empty] | 10v
[6 empty] | Auxiliary circuits > 40 V: 2 kV/60 s/5 kHz |  |  | Percentage deviation | [7 empty] | Control line 1 kV/60 s/5 kHz | [9 empty] | Magnetic fields, external |  | Magneto-motive force, MMF | A
[6 empty] | Control lines 1 kV/60 s/5 kHz | [9 empty] | DIN EN 61000-4-5 | Power cord: 1.2/50μs, 2kV in CM, 1kV in DM | BA1, BA2 | B | – | [8 empty] | 1000 At | Percentage deviation
|  |  |  | SURG | DIN EN 61000-4-5 | Power supply: 1.2/50 μs, 4 kV in CM, 2 kV in DM | BA1, BA2 | B | – | [5 empty] | SURG | (VDE 0847-4-5) | I/O Line: 1kV | [9 empty] | Magnetic fields, technical origin | DIN EN 61000-4-8 | Magnetic flux density | A
[5 empty] | (VDE 0847-4-5) | I/O Line: 1kV | [10 empty] | 1.2 / 50 μs, DM, phase angle 60°, 240° | BA2 | – | B | [7 empty] | (VDE 0847-4-8) | 0.5 mT | Percentage deviation
[6 empty] | 1.2/50 μs, DM, phase angle 60°, 240° | BA2 | – | B | [7 empty] | Current/Voltage Switching: 4kV, 2Ω |  |  | Critical change value / CRC memory areas | [6 empty] | Voltage dips and interruptions | DIN EN 61000-4-11 | Δ U : 100% | B
[6 empty] | Current/Voltage Circuit: 4kV, 2Ω |  |  | Critical change value/CRC memory areas | [7 empty] | Auxiliary circuits > 40 V: 1 kV, 42 Ω | [10 empty] | (VDE 0847-4-11) | Interruption time: 1s | Critical change value / CRC memory areas
[6 empty] | Auxiliary circuits > 40 V: 1 kV, 42 Ω | [10 empty] | Number of pulses: 5 positive, 5 negative | [11 empty] | Number of interruptions 3 | After switching on, the measuring device MUST not have experienced any deterioration in its measuring properties
[6 empty] | Pulse number: 5 positive, 5 negative | [10 empty] | Repetition rate: 1 / min | [11 empty] | Time between interruption: 50 ms
[6 empty] | Repetition rate: 1/min | [9 empty] | DIN EN 61000-4-6 | 150kHz to 80MHz, | BA1, BA2 | A | –
|  |  |  | Conducted | DIN EN 61000-4-6) | 150kHz to 80MHz, | BA1, BA2 | A | – | [5 empty] | Conducted | (VDE 0847-4-6) | 80% AM, 1kHz | [11 empty] | Δ U : 100%
|  |  |  | immunity | (VDE 0847-4-6) | 80% AM, 1kHz | [8 empty] | immunity |  | 3 v | [11 empty] | Interruption time: 20ms
[6 empty] | 10v | [10 empty] | 150kHz to 80MHz, | BA1 | – | A | [8 empty] | Number of interruptions: 1
[6 empty] | 150kHz to 80MHz, | BA3 | – | A | [7 empty] | 80% AM, 1kHz |  |  | Critical change value/CRC memory areas
[6 empty] | 80% AM, 1kHz |  |  | Percentage deviation | [7 empty] | 10v | [11 empty] | Δ U : 50%
[6 empty] | 10V | [9 empty] | – | Magneto-motive force, MMF | BA1 | – | A | [8 empty] | Voltage dip time: 1 min
|  |  |  | Magnetic fields, external |  | Magneto-motive force, MMF | BA3 | – | A | [5 empty] | Magnetic fields, external |  | 1000 At |  |  | Critical change value/CRC memory areas | [8 empty] | Number of interruptions: 1
[6 empty] | 1000 At |  |  | Percentage deviation | [6 empty] | DIN EN 61000-4-8 | 50 Hz, 60 Hz, 30 A/m at I ≤ 32 A | BA1, BA2 | A | –- | [6 empty] | Low-frequency noise immunity |  | 2kHz to 150kHz | B
|  |  |  | Magnetic fields, technical origin | DIN EN 61000-4-8 | 50 Hz, 60 Hz, 30 A/m at I ≤ 32 A | BA1, BA2 | A | – | [5 empty] | Magnetic fields, technical origin | (VDE 0847-4-8) | 100 A/m at I > 32 A | [10 empty] | 11 |  | Percentage deviation
[5 empty] | (VDE 0847-4-8) | 100 A/m at I > 32 A | [10 empty] | Magnetic flux density |  | – | A | [6 empty] | Low-frequency interference emission | DIN EN IEC 61000-3-2 (VDE 0838-2) | Limits | –
[6 empty] | Magnetic flux density | BA3 | – | A | [7 empty] | 0.5 mT |  |  | Critical change value/CRC memory areas | [6 empty] | Interference voltage | DIN EN 55032 | Supply line, I/O line | class B
[6 empty] | 0.5 mT |  |  | Percentage deviation | [6 empty] | DIN EN 61000-4-11 | 40%/ 10/12 cycles | BA1, BA2 | B | – | [7 empty] | (VDE 0878-32)
|  |  |  | Voltage dips and Interruptions | DIN EN 61000-4-11 | 40%/10/12 cycles | BA1, BA2 | B | – | [5 empty] | Voltage dips and interruptions | (VDE 0847-4-11) | 70%/ 25/30 cycles |  | B | [7 empty] | E-field | DIN EN 55032 | 30MHz to 1000MHz | class B
[5 empty] | (VDE 0847-4-11) | 70%/25/30 cycles |  | B | [8 empty] | 0%/ 1 cycle |  | B | [8 empty] | (VDE 0878-32)
[6 empty] | 0%/1 cycle |  | B | [8 empty] | 0%/ 250/300 cycles |  | C
[6 empty] | 0%/250/300 cycles |  | C | [8 empty] | Δ U : 100% | BA2 | – | Critical change value/CRC memory areas
[6 empty] | Δ U : 100% | BA2 | – | B | [7 empty] | Interruption time: 1 s |  |  | After switching-on, the measuring instrument must not have suffered any degradation of its measurement characteristics.
[6 empty] | Interruption time: 1 s |  |  | Critical Change Value / CRC Memory Ranges | [7 empty] | Number of breaks: 3
[6 empty] | Number of interruptions 3 |  |  | After power-on, the measuring instrument should not have experienced any degradation of its measurement characteristics | [7 empty] | Time between breaks: 50 ms
[6 empty] | Time between interruption: 50 ms | [10 empty] | Δ U : 100%
[6 empty] | Δ U : 100% | [10 empty] | Interruption time: 20 ms
[6 empty] | Interruption time: 20ms | [10 empty] | Number of interruptions: 1
[6 empty] | Number of interruptions: 1 | [10 empty] | Δ U : 50%

## Reliability
|  | Orange |  | B.3 Requirements from DIN EN 61581-1 and DIN EN 50470-1 (VDE 0418-0-1) / DIN EN 50470-3 (VDE 0418-0-3)
|  | Yellow |  | C.2 Requirements from DIN EN 50470-1 (VDE 0418-0-1) /
| Spalte1 | Spalte2 | Spalte3 | Spalte4 | Spalte5 | Spalte6 | Spalte7 | Spalte8 | Spalte9 | Spalte10 | Spalte11 | Spalte12 | Spalte13 | Spalte1 | Spalte2 | Spalte3 | Spalte4 | Spalte5 | Spalte6 | Spalte7 | Spalte8 | Spalte9 | Spalte10 | Spalte11 | Spalte12 | Spalte13
| Yellow Spalte2: B.3 Requirements from DIN EN 61581-1 and DIN EN 50470-1 (VDE 0418-0-1) / DIN EN 50470-3 (VDE 0418-0-3) |  | C.2 Requirements from DIN EN 50470-1 (VDE 0418-0-1) /
DIN EN 50470-3 (VDE 0418-0-3)
Phenomenon
Operating temperature | Spalte1: Base; Yellow Spalte2: Conditions; Yellow Spalte3: Utility; C.2 Requirements from DIN EN 50470-1 (VDE 0418-0-1) / Spalte4: Counter; C.2 Requirements from DIN EN 50470-1 (VDE 0418-0-1) / Spalte5: Remarks | Phenomenon | Default | Conditions | Counter | Remarks
Dry heat | Spalte1: DIN EN 60068-2-14 (VDE 0468-2-14); Yellow Spalte2: −30° ± 50°C
| Spalte1: DIN EN 60068-2-2 (VDE 0468-2-2) ,; Yellow Spalte3: In discussion | Dry heat | DIN EN 60068-2-2 (VDE 0468-2-2) , | +70°C ± 2°C, duration 72 h | No damage, no change of content
| Spalte1: tests Bc or Bd |  | test B
| DIN EN 60068-2-2 (VDE 0468-2-2) , | +70°C ± 2°C, duration 72 h |  | No damage, no change of register content
Air humidity, duration Test | Spalte1: test B
| DIN EN 60068-2-78 (VDE 0468-2-78) , | 40ºC ± 2ºC
Air humidity, Cycle | Spalte1: test Cab; Yellow Spalte2: 93% rh, 4 days
Cold test | Spalte1: DIN EN 60068-2-30, test Db; Yellow Spalte2: 40°C for 6 cycles | Humidity, cycle | DIN EN 60068-2-30, test Db | 40°C for 6 cycles | No traces of corrosion
| Spalte1: DIN EN 60068-2-1 (VDE 0468-2-1) ,; Yellow Spalte2: -30 °C ± 3 °C for 16 h | Cold test | DIN EN 60068-2-1 (VDE 0468-2-1) , | Indoor: −25°C ± 3°C | No function | They must not have any damage or alteration to the information and must function properly.
| Spalte1: test Ab |  | test A | Duration: 72 h
| Spalte1: DIN EN 60068-2-1 (VDE 0468-2-1) ,; Yellow Spalte2: method ab,; C.2 Requirements from DIN EN 50470-1 (VDE 0418-0-1) / Spalte4: No function; C.2 Requirements from DIN EN 50470-1 (VDE 0418-0-1) / Spalte5: They must not have any damage or alteration to the information and must function properly. |  |  | Outdoor: −40°C ± 3°C
| Spalte1: test A; Yellow Spalte2: Indoor: −25°C ± 3°C |  |  | Duration: 16 h
Duration: 72 h
Outdoor: −40°C ± 3°C
Sun exposure | Yellow Spalte2: Duration: 16 h
Salt mist test | Spalte1: DIN EN IEC 60068-2-5 (VDE 0468-2-5) , test Sa; Yellow Spalte2: Optional; Yellow Spalte3: In discussion; C.2 Requirements from DIN EN 50470-1 (VDE 0418-0-1) / Spalte4: Procedure B | Sun exposure | DIN EN IEC 60068-2-5 VDE 0468-2-5) , | Optional | Procedure B
Protection class test | Spalte1: DIN EN IEC 60068-2-52 (VDE 0468-2-52) , test Kb, level 1; Yellow Spalte2: Optional |  | test Sa,
| Spalte1: DIN EN 60529; Yellow Spalte3: No function; C.2 Requirements from DIN EN 50470-1 (VDE 0418-0-1) / Spalte4: Indoor: IP51; C.2 Requirements from DIN EN 50470-1 (VDE 0418-0-1) / Spalte5: Penetration might only occur in an amount that does not interfere with operation, an insulation test must be passed. | Protection class test | DIN EN 60529 |  | Indoor: IP51 | Penetration might only occur in an amount that does not interfere with operation, an insulation test must be passed.
Mechanical impact | Spalte1: (VDE 0470-1); C.2 Requirements from DIN EN 50470-1 (VDE 0418-0-1) / Spalte4: Outdoor: IP54 |  | (VDE 0470-1) |  | Outdoor: IP54
| Spalte1: DIN EN 60068-2-75 (VDE 0468-2-75) (severity); Yellow Spalte2: Impact energy value 20 J (5 kg at 0.4 m) | Mechanical impact | DIN EN 60068-2-75 (VDE 0468-2-75) , Ehb | Impact energy value 0.2 J | meter cover, terminal cover
| DIN EN 60068-2-75 (VDE 0468-2-75) , | Impact energy value 0.2 J |  | meter cover, terminal cover
Shock test | Spalte1: Ehb
| Spalte1: DIN EN 60068-2-27 (VDE 0468-2-27) ,; Yellow Spalte2: Half-sine pulse, peak acceleration: 30 gn(300 m/s 2 ),; C.2 Requirements from DIN EN 50470-1 (VDE 0418-0-1) / Spalte4: No function; C.2 Requirements from DIN EN 50470-1 (VDE 0418-0-1) / Spalte5: No damage, no change in information, no functionality | Shock test | DIN EN 60068-2-27 (VDE 0468-2-27) , test Ea | Half-sine pulse, peak acceleration: 30 gn (300 m/s 2 ), | No function | No damage, no change in information, no functionality
| Spalte1: test Ea; Yellow Spalte2: Pulse duration: 18 ms |  |  | Pulse duration: 18 ms
[14 empty] | Vibration (sine) | DIN EN 60068-2-6 (VDE 0468-2-6) , | Frequency range: 10 Hz to 150 Hz, crossover frequency. 60Hz; | No function | No damage, no change in information, no functionality
[15 empty] | test Fc | f < 60 Hz: constant movement amplitude 0.075 mm
f > 60 Hz: constant acceleration, 1 gn (10 m/s 2 )
Single point control, 10 passes